## Byuildling A Remodel RFI LOG
RFI# | Date Received | Contractor | Questions | Date Responded | Response
1 | 2025-06-30 | Black Hall Construction | Sheet P3 at exam rooms 2 & 3 show new sinks. There is no description of this fixture. Please give fixture description, make, model, faucet, etc. | 2025-07-01 | COUNTERTOP WITH INTEGRAL SINK FURNISHED UNDER THE SOLID COUNTERTOP SPECIFICATION SECTION. JUST J35FS FLAT GRID STRAINER. CHICAGO "HYDRONIC" "ECAST" #116.303.AB.1 SINGLE HOLE (OR T&S BRASS OR ZURN EQUAL). DUAL BEAM SENSOR OPERATED, 120V/1Ø ELECTRIC POWERED FAUCET WITH 12 VOLT A.C. TRANSFORMER. 5-1/4” RIGID/SWING GOOSENECK SPOUT WITH 1.5 GPM LAMINAR FLOW NON-AERATING OUTLET. LEONARD #170A-LF, POINT OF USE THERMOSTATIC MIXING VALVE. CONNECTIONS SIZES: SOIL OR WASTE 2", VENT 1 1/2", DOMESTIC COLD WATER 1/2", DOMESTIC HOT WATER 1/2". SEE ADDENDUM 3.
2 | 2025-06-30 | Black Hall Construction | Sheet P3 @ exam rooms 2 & 3 shows an H-1 at both exam rooms. The North Shows a note 3, the South room does not show a note 3. Please clarify, are the water heaters necessary? The building has a hot water system. | 2025-07-01 | The electric water heater originally shown serving Exam Rooms 2 and 3 (Sheet P-3) shall be removed from the project scope. All associated electrical and plumbing connections shown in the construction documents related solely to this water heater are to be omitted. Any necessary re-routing of affected services shall be coordinated in the field and submitted for review if required. SEE ADDENDUM 3.
3 | 2025-06-30 | Black Hall Construction | Sheet P3 keynote 4 states “expose all utilities to wall behind existing sink” for the north exam room. No such note for the south exam room. Is this piping to be exposed on the wall behind the existing sink? Or should this note read “expose all utilities in wall behind existing sink?” | 2025-07-01 | Keynote 4 should read: “Expose all utilities in wall behind existing sink” This applies to both the North and South Exam Rooms. SEE ADDENDUM 3
4 | 2025-07-07 | DANIAR Construction Group | Is the Owner or your district taking care of the Fire Alarm company and any work they need to do as necessary or the contractor is responsible and if the contractor needs to arrange. Could you inform us regarding the company that is currently managing this service. | 2025-07-08 | FIRE SPRINKLER MODIFICATIONS: Contractor shall include repositioning of fire sprinkler heads as required to accommodate new ceiling layout and architectural features. Contractor is responsible for all coordination with the fire sprinkler company, including scheduling, scope of work, and ensuring compliance with applicable codes, permits and any other requirements. Preferred fire sprinkler company: RLH Fire Protection Bakersfield Office 4300 Stine Road Bldg. 500 Bakersfield, CA 93313 Phone: (661) 322-9344 Elizabeth Norton enorton@rlhfp.com
5 | 2025-07-07 | DANIAR Construction Group | Is there a maintenance company working on your emergency generator? Will they be contracted by the owner or we need to include it in our bid. | 2025-07-08 | EMERGENCY GENERATOR SYSTEM: Scope of work shall not add any additional load to the existing emergency generator system. No modifications to the emergency power system are required under this project.
6 | 2025-07-07 | DANIAR Construction Group | The shut off line to your Fire Sprinklers: Does it have a Zone we can disconnect or the full system will need to be emptied. | 2025-07-08 | FIRE SPRINKLER COORDINATION: Contractor shall coordinate all required fire sprinkler modifications or adjustments during construction with the Owner, as directed by the fire sprinkler contractor. Coordination shall include scheduling, access, and any necessary approvals.
7 | 2025-07-07 | DANIAR Construction Group | Could you identify the company you originally purchased the Cabinets from for this project | 2025-07-08 | Cabinetry Contractor: C & W Custom Cabinets Inc. 813 West Ave. L-8 # B Lancaster, Ca. 93534 6612-942-5311
8 | 2025-07-07 | DANIAR Construction Group | Could you identify the company that provided your Doors, Door Frames and Windows. | 2025-07-08 | DOORS AND WINDOWS: Kern Glass 3701 Gulfstream Lane Bakersfield, CA 93308 (661) 327-4053
9 | 2025-07-07 | DANIAR Construction Group | Regarding your stone counter. Do you need to match the same product if so please indicate the name if possible. for the counter and the Desk. | 2025-07-08 | COUNTERTOP FINISH MATCHING: Match existing material and finish where replacements or extensions are required. If the original material is no longer available, provide a similar surface material and finish for review and approval by Owner prior to installation. Owner does not have specifications or product information for the existing countertop material. All countertops were installed by C & W Custom Cabinets Inc.
10 | 2025-07-07 | Black Hall Construction | Please clarify if the window frames are storefront frames or hollow metal frames. | 2025-07-09 | See addendum 4.
11 | 2025-07-07 | Black Hall Construction | Please clarify what type of x-ray window glass needs to be used. | 2025-07-09 | Clarification – Exam Room 1 Shielding Note: The reference to “windows” in the shielding note for Exam Room 1 was included as part of a general description. There are no windows in Exam Room 1, and no x-ray glass is included in the scope of this project. Lead lining requirements apply only to the door and walls, as indicated and per the Physicist’s Shielding Report and Plan.
12 | 2025-07-09 | Black Hall Construction | The one-way glazing performance will vary with lighting conditions, and cannot be guaranteed satisfaction. Please provide a specification. | 2025-07-09 | Contractor shall coordinate with the Owner at the time of selection to confirm requirments and finalize details.
13 | 2025-07-09 | JTS Construction | 1. Please provide all bid forms required to be submitted at the time of bid. Currently only the Bid Proposal form has been provided. We are still missing the Statement of Bidders Qualifications, List of Subcontractors, Bid security form and Non-collusion Declaration that are listed as required. | 2025-07-10 | Statement of Bidders Qualifications, List of Subcontractors, Bid security form and Non-collusion Declaration Forms were missing from the bid packet. Those documents are now posted on our website for review. https://www.wshcd.org/public-bidding
14 | 2025-07-10 | JTS Construction | Please confirm that RLH will be contracted directly with you, the owner? This means we will not include their costs in our proposal. | 2025-07-10 | The Owner does not have any existing contracts for the Fire Sprinkler modification required for this project. The contractor shall contract directly with RLH to complete all necessary work required of the contract and shall be responsible for scheduling, scope of work, and ensuring compliance with applicable codes, permits and any other requirements. All associated costs should be included in the contractos proposal.
15 | 2025-07-08 | Black Hall Construction | As per Sheet A-4 Room Finish Schedule, we are to provide Vinyl Plank in the Administration are and Rubber Sheet in the Exam Room. However, the finish specifications provided on Sheet A-2 indicate Carpet and Sheet Vinyl in these areas, which does not match the Room Finish Schedule. Could you please confirm which finish takes precendence and whether any specific manufacturer, style, and colo have been specified? Or should we proceed with indisutry-standard selections? Could you please confirm the type of concrete finish required in the Reception and Reception Office areas? Sepcifically, is the finish intended to be Polished or Sealed Concrete? | 2025-07-10 | See addendum 5.
16 | 2025-07-09 | JTS Construction | Please advise what items are to be salvaged and advise of any work that will be provided/performed by the Owner? At the jobwalk it was stated that the wallpaper in the front lobby at the Administrative Office will be provided and installed by the owner. Please confirm. | 2025-07-10 | Contractors are advised to salvage any countertops, cabinets, door, hardware and any other materials in working order to be used in other areas of the remodel. Particularly items to evaluate salvage would be cabinets, hardware, sink, faucets and other items in Reception Office and Exam Room. Prior to construction Owner shall remove at its cost soap dispensers, paper towel dispensers, hand sanitizer dispensers, wall hung items, medical and non-medical equipment and room signage from the construction area. Owner shall be responsible for purchasing and installing all similar items. Repair and replacement of the wall paper in the lobby will be completed by the owner outside of the construction contract.
17 | 2025-07-09 | JTS Construction | 1. Please confirm that the owner will pay the cost of any additional tariff’s on materials that the federal government assesses after the bid date but before materials can be ordered. Since as of yesterday everyone knows the current amount of tariff’s the federal government is assessing other countries all suppliers, subcontractors and general contractors should be including those costs in their bids. However, no-one can know what tariff’s other countries may retaliate with and if that occurs the federal government has said it will reciprocate by increasing the tariff against that country even more. If that occurs and materials for this project come from that country and are assessed additional tariff’s we want to make sure that the owner will pay for that additional cost that no-one can foresee. If the owner does not pay for that potential additional tariff cost every bidder will need to assume the worst and double their material prices. | 2025-07-11 | To address the above question, the District will be adding the following provision by addendum into the form of Agreement to be entered into with the lowest bidding Contractor for this Project (in the event that the District elects to proceed to contracting per the bid notice): In the event of a Significant Price Change for Materials (as defined below) occurring at any time during the performance of the Contract, the Contract Sum shall be equitably adjusted by Change Order in accordance with the procedures of the Contract Documents as well as those set forth herein (a 'Price Escalation Change Order'). As used herein, a 'Significant Price Change for Materials' means a change in price of one or more items of material to be included in the Work if (a) the price of the material increases or decreases by 5 percent (5%) or more in between the date of this Contract and the date of installation; (b) the price increase or decrease is solely the consequence of a tariff imposed or adjusted on the material; and (c) the applicable tariff is first imposed or adjusted, as applicable, after contract execution. In order to receive a Price Escalation Change Order, the Contractor shall provide to the Owner, in writing, prior to the time of execution of this Agreement, its estimated costs for the relevant materials that it believes may be subject to potential escalation under the above provisions (the 'Contractor's Escalation List'). The Contractor's Escalation List shall be made an exhibit to this Agreement. Prior to purchasing any of the materials listed in Contractor's Escalation List, the Contractor must provide the Owner with at least two (2) timely written proposals from suppliers as well as a reputable third-party price index to confirm the credibility of the proposals. If the pricing escalation cannot be avoided through commercially reasonable procedures, the parties may enter into a change order in the amount of the lowest cost proposal or price index amount. Any such change order(s) shall not include overhead or profit mark-ups on the increase(s) from either the Contractor or its Subcontractors. Any failure to include a material in the Contractor's Escalation List shall automatically be deemed a waiver of the right to seek a price escalation for the applicable materials without the Owner’s prior written consent (which consent may be withheld in the Owner’s sole and absolute discretion). If prices for materials listed on Contractor' Escalation List decrease by five percent (5%) or more from what was in the Contractor’s original estimate, the Owner shall be entitled to a corresponding deduction in the Contract Sum.
18 | 2025-07-10 | Black Hall Construction | The addendum says "Aluminum storefront framing to match adjacent glazing systems in profile and finish." What exactly are we matching? | 2025-07-11 | See Addendum 6.
19 |  | JTS Construction | Please provide detailed information on how the soundproofed wall shall be constructed for Room R01 | 2025-07-11 | ADMINISTRATION (RO1) WALL UPGRADE: Where noted, upgrade existing 1-hour fire-rated wall (UL U419) constructed of 2x4 steel studs with 5/8" Type X gypsum board each side, full height to structure, as follows: Install 3-1/2" thick mineral wool insulation (noncombustible, Thermafiber Fire & Sound Guard or equal) within the stud cavity. Seal all perimeter joints (floor, roof deck, wall intersections) and all penetrations using UL-classified acoustical firestop sealant (Hilti CP 506 or equal). Apply fire-rated putty pads to the backs and sides of all electrical boxes. Avoid back-to-back box placement. Add a second layer of 5/8" Type X gypsum board to the administration side of the wall, offset joints from the first layer. Attach per UL U419 guidelines using approved fastener spacing and installation sequence. Maintain all construction per UL Design No. U419 to preserve 1-hour fire rating. Final wall assembly shall achieve minimum STC 45.
20 | 2025-07-09 | JTS Construction | Room R01 has a relocated door going into a soundproofed wall. Is that existing door sound resistant as if it is a regular door soundproofing the wall will not do any good in which case the door should be replaced with a sound resistant door, frame and hardware set. | 2025-07-11 | CORRECTION: ADMINISTRATION (RO1) SOUND RESISTANT DOOR SOUND-RATED DOOR – STC 45: Provide STC 45-rated interior sound-resistant door assembly at locations noted. Assembly shall include: Door Leaf: 1-3/4" thick solid-core wood or metal acoustical door, factory-certified to STC 45 per ASTM E90/E413. Frame: 16 ga. hollow metal frame, compatible with acoustical seals, installed per manufacturer’s tested assembly. Seals: Continuous perimeter acoustic seals at head and jambs. Automatic Door Bottom: Surface-mounted or mortised drop seal. Threshold: Sound-rated threshold with neoprene or silicone seal. Hardware: Grade 1 lever set, ball-bearing hinges, and door closer (as required). All components shall be part of a tested STC 45 assembly and installed to prevent sound flanking. Final installation subject to Owner approval.
21 | 2025-07-09 | JTS Construction | Do the existing walls of Room R01 go to the roof deck as if not the ceiling should receive sound insulation above the t-bar. | 2025-07-11 | Yes, walls in Room RO1 extend to the roof structure. See response to RFI 19.
21 | 2025-07-09 | JTS Construction | Please provide a specification for the new sinks and acoustical ceiling/tiles. | 2025-07-11 | See Addendum 3 for exam room sink specifications. ADMINISTRATION (RO1) ACOUSTICAL T-BAR CEILING (REPLACEMENT): Remove existing ceiling system in its entirety. Provide new suspended acoustical T-bar ceiling system. Install industry-standard 15/16" exposed grid with 2'x2' or 2'x4' lay-in acoustical ceiling tiles, minimum NRC 0.55 and CAC 35, suitable for interior office applications. Tile finish, texture, and color shall match existing or be selected to closely resemble adjacent finishes. Final tile and grid selection shall be subject to Owner approval.
23 | 2025-07-09 | JTS Construction | Please provide specifications for all finishes we are to match. This includes casework, flooring, and FRP. | 2025-07-11 | GENERAL NOTE – PRODUCT SELECTIONS IN ABSENCE OF SPECIFICATIONS: Where product specifications are not provided by the Owner, Contractor shall provide materials and products that match existing where applicable, or select suitable industry-standard products appropriate for office-type applications. Selected items shall match the quality, functionality, and color of adjacent or similar materials to the greatest extent possible. Additional site visits are permitted and encouraged to assist in achieving the best match. All selections shall be verified and approved by the Owner prior to ordering or installation. See Also, Addendum 5 - Floor Finishes
24 | 2025-07-09 | JTS Construction | Please advise what items are to be salvaged and advise of any work that will be provided/performed by the Owner? At the jobwalk it was stated that the wallpaper in the front lobby at the Administrative Office will be provided and installed by the owner. Please confirm. | 2025-07-11 | Further clarification to RFI 16. GENERAL NOTE – RFIs, SUBSTITUTIONS & SALVAGE: All Requests for Information (RFIs), product substitutions, or deviations from specified materials shall be submitted for review and are subject to Owner approval. Products and materials designated for demolition shall be carefully removed and salvaged to the extent possible. Salvageable items may include, but are not limited to, cabinetry, plumbing fixtures, countertops, doors, and hardware. Coordinate with Owner prior to removal to determine items to be retained, relocated, reused, or discarded.
25 | 2025-07-09 | Memon Builders | As seen on the plan, we are to relocate the door, and I would like to confirm the following regarding callouts 1-LN and 1-LW For 1-LN, the detail appears to call for a new door and window installation. For 1-LW, the detail shows a new fixed glass occupying a larger portion of the wall. Are we required to change wall (4) to a new soundproof wall as specified in the floor plan schedule Can you kindly confirm if all walls are to be replaced as shown in the detailed drawings on Sheet A-5? | 2025-07-11 | SEE ADDENDUM 7 CORRECTION - ADMINISTRATION (R01): PROVIDE STC 45 SOUND-RATED DOOR ASSEMBLY The original note stating "Relocate Existing Door" is revised as follows:... For 1-LN, the detail appears to call for a new door and window installation. THE DOOR SHOWN ON SHEET A-4, IN ELEVATION 1-LN, ROOM 1 - ADMINISTRATION - LOBBY SIDE, IS TO THE CORRIDOR AND IS NOT A PART OF THIS PROJECT. For 1-LW, the detail shows a new fixed glass occupying a larger portion of the wall. THIS WINDOW WILL BE ONE WAY VIEWING FROM THE ADMINISTRATION OFFICE TO THE LOBBY Contractor shall coordinate with Owner at the time of selection to confirm requirements and finalize details. Are we required to change wall (4) to a new soundproof wall as specified in the floor plan schedule Can you kindly confirm if all walls are to be replaced as shown in the detailed drawings on Sheet A-5? SEE ADDENDUM 7, CLARIFICATION - ADMINISTRATION (RO1) WALL UPGRADE
26 | 2025-07-11 | Memon Builders | During the job walk, it was mentioned to provide privacy glass on both sides of the reception as shown in green above. Please confirm if the privacy glass is also required on the door. Additionally, kindly provide the specification for the privacy glass, including type, model, and height. | 2025-07-12 | The panels nearest the wall are solid panel to match adjacent. The panel closes the front door glass panel temp. See plans A-5, Room 5, Interior Elevations # 18 and #26. SEE ADDENDUM 9 FOR SEPCIFICATIONS